## Slide 1: Renewable Scenario in Karnataka
Er. Dilip Kumar R.V
Chief Engineer(Ele.)
SLDC,Karnataka

## Slide 2: KARNATAKA GENERATION DETAILS
Sl No | Generation | Installed Capacity(MW)
1 | KPCL-THERMAL | 5020
2 | KPCL-MAJOR HYDRO | 2395
3 | KPCL- MINOR HYDRO | 1393
4 | CGS | 3693
5 | UPCL | 1200
6 | SMALL THERMAL | 929
7 | NCEP | 11740.2
 | TOTAL | 26370.2
Chart: 
| KPCL-THERMAL | KPCL-MAJOR HYDRO | KPCL- MINOR HYDRO | CGS | UPCL | SMALL THERMAL | NCEP
Installed Capacity(MW) | 5020 | 2395 | 1393 | 3693 | 1200 | 929 | 11740.2

## Slide 3: NCEP Details-KARNATAKA
NCEP TYPE | No. of Plants | Installed Capacity (MW)
Mini Hydel | 80 | 815.085
Biomass | 20 | 136.86
Co-gen | 65 | 1520
Solar | 284 | 4848.56
Wind | 100 | 4419.695
Total | 549 | 11740.2
Chart: 
| Mini Hydel | Biomass | Co-gen | Solar | Wind
Installed Capacity(MW) | 815.085 | 136.86 | 1520 | 4848.56 | 4419.695

## Slide 4: Wind & Solar Installed Capacity Details -Voltage wise Capacity
NCEP Type | 220kV | 110kV | 66kV | 33kV | 11kV | Total | SCADA connected | %SCADA integrated
Solar | 1354 | 1524.675 | 1473.88 | 230 | 266 | 4848.56 | 4409.55 | 90.95
Wind | 1855.9 | 1306.65 | 966.395 | 269.61 | 21.14 | 4419.695 | 4398.895 | 99.53

## Slide 5
BNG-TRZ
MYS-TRZ
HSN-TRZ
BGK-TRZ
MFTDMA IF
BNG-TRZ
MYS-TRZ
HSN-TRZ
BGK-TRZ
RC
1-111
TMK-TRZ
MYS-TRZ
BGK-TRZ
GLB-TRZ
RC
1-87
RC
1-108
RC
1-63
GSAT 16
EB-EA
ALDCs
BESCOM
MESCOM
HESCOM
GESCOM
BESCOM
MESCOM
HESCOM
GESCOM
DCCs
MON.SYS
MAIN LDC
BNG DA SYSTEM
MCC-1
MCC-2
OACs
CESC
CESC
TMK-TRZ
GLB-TRZ
TMK-TRZ
GLB-TRZ
BNG-TRZ
RC
1-67
HSN-TRZ
RC
1-153
EXISTING RF
DRMCC-1
DRMCC-2
EB-EA
DISASTER RECOVERY LDC
KPTCL SCADA System Architecture
16 control centers, which includes the Main control centers, a Disaster Recovery centre, Area load dispatch centers for the Transmission Zones and Distribution control centers for the ESCOMs.
All the Transmission RTUs communicate to MCC-1 & Distribution RTU’s communicate to MCC-2
The total system is configured with 72 servers and 115 operator workstations
Communication is on a owned VSAT HUB and Leased Lines for Inter control Centre Communication as main and VSAT as secondary
Notes: 5

## Slide 6: SCADA DATA flow
Conventional Station
Control panel
RTU
VSAT
HUB
Main Control centre
SAS Station
VSAT
Gateway
Satellite
GSAT 16
D R HUB
D R Control centre

## Slide 7: Communication network
Largest VSAT network with 1400 nodes(stations)
Can handle upto 1600 RTUs on IEC 60870-5-104 protocol.
New Conventional Sub-station can be brought into SCADA coverage by providing RTU and VSAT.
Integration of Sub-Station Automation systems to SCADA system on IEC 104 protocol by providing VSAT.
AMR solution with existing VSAT Network.
Voice communication to all nodes over VSAT.
To provide all relevant data to RLDC & NLDC on ICCP

## Slide 8: KARNATAKA STATE policy for RE integration
RE generators irrespective of the voltage class
has to radial connect to the nearest KPTCL station having Tariff meter at KPTCL premises as shown below
POOLING STATION
KPTCL SUB STATION
SCADA MONITOR AND TARIFF POINT
SCADA MONITOR AND TARIFF POINT
FEEDERS
FEEDERS
POOLING STATION
11kV
110 or 66 kV

## Slide 9: KARNATAKA-Real time Renewable Generation Monitoring

## Slide 10: Pavagada Solar park : 2000MW(Commissioned 600MW)

## Slide 11: Solar generation injection to STATE GRID

## Slide 12: Solar Generation in BESCOM Area

## Slide 13: Wind Generation in HESCOM Area

## Slide 15: Solar Daily Peak Curve
Chart: 

## Slide 16: Wind Daily Peak Curve
Chart: 

## Slide 17: KERC Regulations 2015
Implementation of Forecasting, Scheduling, Deviation settlement Mechanism of Wind and Solar

## Slide 18: Main points of KERC regulations on Wind and Solar
Notification issued on 31st May 2016
Regulations come into force with commercial implication from 1-June-2017
All Wind Generators above 10 MW and all Solar Generators above 5 MW at the pooling station level come under the purview of these regulations
Wind and solar generators coming under the purview of the regulations, either by themselves or through their Aggregator/QCA, are providing week ahead, day ahead schedules to SLDC, with a provision of revising the schedules 16 times intra-day.

## Slide 19: Coverage and Status of RE-DSM Mechanism (Schedule being received) as on 10.04.2018
Pooling stations | Under regulations Nos | Schedules received Nos | Capacity for schedules received MW | Total Capacity MW
Wind | 76 | 73 | 3849.28 | 3998.68
Solar | 108 | 103 | 3203.88 | 3258.88
Total | 184 | 176 | 7053.16 | 7257.56
No. of Aggregators : 10
(The above numbers are for wind pooling station of 10MW and above and solar pooling station of 5 MW and above)

## Slide 20: Deviation Settlement Mechanism
All Wind generators above 10 MW and Solar generators above 5 MW at the pooling station level come under the purview of DSM.
% error (deviation) to be calculated as under
  % error (deviation)= (Act Gen – Sch Gen) x 100)
  Available capacity (AvC)
The details of AvC shall be provided by the Generators or their aggregator as per the formats prescribed by SLDC
Permissible deviation is + or – 15% (85% to 115% allowable)
Energy charges payable
  As per actual Energy supplied irrespective of schedule for Intra State transactions
  As per scheduled Energy for Inter State transactions which are governed by CERC

## Slide 21: DSM charges
Deviation range Payment by Gen to DSM account
> ± 15% and ≤ ± 25% Rs.0.50 per kWh
> ± 25% and ≤ ± 35% Rs.0.50 per kWh upto ± 25% + Rs.1.00 per kWH for balance
> ± 35% Rs.0.50 per kWh upto ± 25% + Rs.1.00 per kWH upto ± 35% +
Rs.1.50 per kWH for balance
SLDC to maintain pool of DSM charges

## Slide 22: Wind Deviation Trend
Chart: TOTAL WIND DEVIATION ON 25-04-2018

## Slide 23: Solar Deviation Trend
Chart: TOTAL SOLAR DEVIATION ON 25-04-2018

## Slide 24: Thank You