## Slide 1: Receipt of Real-time / Daily RE Generation Data
B. B. Mehta,
SLDC, Gujarat
04.05.2018

## Slide 2
2
Wind generation 5575 MW
Solar Generation 1493 MW
As on March 2018
Notes: 2

## Slide 3
    RE Data Techniques & Process

## Slide 4
  Field level
    DAS meter at STU s/s - recording export and import energy from s/s panels with RS 485 serial port facility
    KW/KWh, KVA/KVAh, KVAR/KVARh and /or PF and Tamper events etc.
    0.5S Accuracy class
    Provision for peak, night & rest hour
    E - watchlite software – fetch the reading
  RE station / plant level
    ABT meter - 15 minute block wise reading
    MW (15 minute), MVAR (per day cumulative), Frequency
    0.2S Accuracy class
    Stored reading for 10 days to 35 days
    MRI (Meter Reading Instrument) – for download of ABT reading
RE Data - Informative & Accounting

## Slide 5
  Before May 2015:
  As per point of connectivity, main meter and check meter was provided at sending end and receiving end visa e versa.
  After May 2015:
  Main & Check meter should be provided at receiving end (GETCO End).
  Type of Meter:
  “A” Type meter – 0.2S class.
  “B” Type meter – if connection at and below 33KV level.
  Approved meter make : L&T, Secure, Wallaby
RE Data - Metering arrangement

## Slide 6
    Monthly RE Generation
    Informative Data

## Slide 7
Installed capacity (MW) and Generation (MUs) from renewable resources (Injected in to the GRID) |  |  |  |  |  |  |  | 
Sr. No. | Month |  | Renewable energy sources | Installed Capacity (MW) | Generation in Mus during the month | Cumulative generation in Mus during the year (1st April'17 onwards) | Generation in Mus during the corresponding Month of last year | Cumulative generation in Mus up to the corresponding month of last year 1st April'16 onwards
1 | Apr-17 |  | Wind | 5318.38 | 947.36 | 947.36 | 500.28 | 500.28
2 |  |  | Solar | 1229.60 | 186.25 | 186.25 | 170.97 | 170.97
3 |  |  | Biomass | 41.10 | 2.69 | 2.69 | 0.23 | 0.23
4 |  |  | Pvt. Mini Hydro | 8.56 | 4.41 | 4.41 | 2.01 | 2.01
Total |  |  |  | 6597.64 | 1140.71 | 1140.71 | 673.49 | 673.49
1 |  | May-17 | Wind | 5348.25 | 1241.50 | 2188.86 | 992.25 | 1492.53
2 |  |  | Solar | 1229.60 | 186.80 | 373.05 | 165.63 | 336.60
3 |  |  | Biomass | 41.10 | 1.96 | 4.66 | 0.06 | 0.29
4 |  |  | Pvt. Mini Hydro | 8.56 | 1.82 | 6.22 | 0.00 | 2.01
Total |  |  |  | 6627.51 | 1432.08 | 2572.79 | 1157.94 | 1831.42
Above RE data is submitting by 10th of every month by SLDC
Monthly Information to CEA

## Slide 8
Above RE data is submitting by 10th of every month by SLDC
Installed capacity (MW) and Generation (MUs) from renewable resources (Injected in to the GRID) |  |  |  |  |  |  | 
Sr. No. | Month | Renewable energy sources | Installed Capacity (MW) | Generation in Mus during the month | Cumulative generation in Mus during the year (1st April'17 onwards) | Generation in Mus during the corresponding Month of last year | Cumulative generation in Mus up to the corresponding month of last year 1st April'16 onwards
1 | Mar-18 | Wind | 5574.75 | 672.96 | 9635.62 | 590.57 | 7719.99
2 |  | Solar | 1493.31 | 230.67 | 2048.39 | 176.44 | 1738.27
3 |  | Biomass | 41.10 | 4.21 | 32.66 | 2.08 | 12.20
4 |  | Pvt. Mini Hydro | 20.56 | 4.84 | 42.92 | 3.92 | 27.55
Total |  |  | 7129.72 | 912.67 | 11759.60 | 773.01 | 9498.01
Monthly Information to CEA

## Slide 9
    Monthly RE Generation
    Accounting Data

## Slide 10
The RE data is based on Renewable energy certified by SLDC
 |  | Installed Capacity(MW) as on Last date of the Month April-17 |  |  | Generation (MU) During the Month April-17 |  |  | Cumulative Generation (MU) During the Current Financial Year(From April-till reporting Month) |  | 
Sl. No | Renewable resources | Central Sector | State Sector | Private Sector | Central Sector | State Sector | Private Sector | Central Sector | State Sector | Private Sector
1 | Wind |  | 3584.0 | 1707.9 |  | 644.7 | 307.4 |  |  | 
2(a) | Solar (Above 1 MW) | 46.0 | 1171.5 | 20.5 | 8.3 | 171.0 | 3.2 |  |  | 
2(b) | Solar (Less than 1 MW) |  | 1.5 |  |  | 0.2 |  |  |  | 
3 | Biomass |  | 43.3 |  |  | 4.9 |  |  |  | 
4 | Bagasse (Suger Mill & Others) |  | 20.8 |  |  | 0.0 |  |  |  | 
5 | Small Hydro (Up to 25 MW) |  | 8.6 |  |  | 4.4 |  |  |  | 
6 | Any Other (Please specify the Resources) wind with NO PPA |  |  | 24.3 |  |  | 2.4 |  |  | 
 |  | 46.0 | 4829.7 | 1752.7 | 8.3 | 825.2 | 313.0 |  |  | 
Monthly Information to CEA

## Slide 11
 |  | Installed Capacity(MW) as on Last date of the Month Mar-18 |  |  | Generation (MU) During the Month Mar-18 |  |  | Cumulative Generation (MU) During the Current Financial Year(From April 17 - till reporting Month) |  | 
Sl. No | Renewable resources | Central Sector | State Sector | Private Sector | Central Sector | State Sector | Private Sector | Central Sector | State Sector | Private Sector
1 | Wind |  | 3739.60 | 1810.85 |  | 466.21 | 205.73 |  | 6538.69 | 3047.90
2(a) | Solar (Above 1 MW) | 46 | 1277.4 | 56 | 8.175 | 212.81 | 9.21 | 78.04 | 1867.65 | 58.531
2(b) | Solar (Less than 1 MW) |  | 1.50 |  |  | 0.23 |  |  | 2.03 | 
3 | Biomass |  | 39.90 |  |  | 4.15 |  |  | 52.07 | 
4 | Bagasse (Suger Mill & Others) |  | 20.80 |  |  | 6.45 |  |  | 25.11 | 
5 | Small Hydro (Up to 25 MW) |  | 8.60 |  |  | 4.10 |  |  | 44.78 | 
6 | Any Other (Please specify the Resources) wind with NO PPA |  |  | 24.30 |  |  | 2.76 |  |  | 42.571
 | Total | 46.00 | 5087.80 | 1891.15 | 8.175 | 693.9 | 217.7 | 78.04 | 8530.34 | 3149.011
The RE data is based on Renewable energy certified by SLDC
Monthly Information to CEA

## Slide 12
  SLDC publish Wind Energy Certificate based on Energy allocation received from GEDA,
  from Energy recorded in ABT meter of pooling station,
  on or before 20th of every month for preceding month.
  Pooling station wise, Energy meter data is received between first Monday and first Wednesday of last week of previous month.
  After validation these data is sent to GEDA, GEDA allocate the energy entity wise and “allotted entity wise energy” is received by SLDC latest by 15th - 16th working day.
  Based on this allocated energy (1400 entity for 70 pooling stations) this office publishes wind energy certificate.
  In view of above, SLDC can furnish the required Generation Details for preceding month in last week of the current month.
Real-time Wind Generation Data Communication

## Slide 13
    Real-time RE Generation Data

## Slide 14
Substation / RTU Location
CT
PT
Transducer
MW,MVAR
Transducer
Votage,
Frequency
CMR
CMR
D20
Processor
Status Card
Control Card
Analog Card
RTU
R
S
2
3
2
C
o
m
m
u
n
i
c
a
t
i
o
n
p
o
r
t
MODEM
MUX
PLCC
COMMUNICATION
Sub SLDC
CB
Isolator
GETCO
Lease Line / Microwave

## Slide 15
  Communication link between Solar Power Station and STU EHV Sub-Station, where RTU is installed.
  Radio Modem is also provide for point to point speech communication between Solar Plant and RTU end of GETCO.
  The Radio Modem frequency band is 2.412 to 2.464 GHz which is Unlicensed Band.
  The total Equipment cost of 1 set is around Rs. 3.5 Lacs for Solar data acquisition system.
  Developers readily agreed to bear cost including maintenance.
Type of communication | Radio Modem | GSM/GPRS
Total Nos. | 76 | 3
Real-time Solar Generation Integration

## Slide 16
  Communication link like Radio / GSM /GPRC -between Solar Power Station and GETCO EHV Sub-Station, where RTU is installed.
  Radio Modem is also provided for point to point speech communication between Solar Plant and RTU end of GETCO.
  The Radio Modem frequency band is 2.412 to 2.464 GHz which is Unlicensed Band.
  The total Equipment cost of 1 set is around Rs 3.5 Lacs for Solar data acquisition system.
  Developers readily agreed to bear cost including maintenance.
Real-time Solar Generation Data Communication

## Slide 17
Real-time Wind Generation Data Integration

## Slide 18
  Data connectivity is established between Wind Power Station and GETCO End Sub-Station for RTU with mix of available Technologies. i.e. like Radio / GSM /GPRS / PLCC / Lease Line.
  Repeater utilized to fetch the data of long distant.
The total cost of 1 set is around Rs. 6 Lacs for Wind data acquisition system including RTU and communication equipment.
  Developers readily agreed to bear cost including maintenance.
Real-time Wind Generation Data Communication

## Slide 19
Real-time Wind Generation Data Communication
PLCC
MUX
MODEM
Operating
System
Data Concentrator
Front End
Processor
(FEP 1 & 2)
R
J
4
5
L
A
N
C
o
n
n
e
c
t
i
o
n
10/100MBPS HUB
ROUTER
OFC WIDE
BANK
COMMUNICATI
ON
State Load Dispatch Center
AP 01
AP 02
Work Stations / Servers
LOCAL AREA NETWORK
GETCO
Lease Line / Microwave

## Slide 20
  IEGC clause 5.2(u) Special requirements for Solar/ wind generators:
  “System operator (SLDC/ RLDC) shall……. For this, Data Acquisition System facility shall be provided for transfer of information to concerned SLDC and RLDC.”
  IEGC clause 6.2
  “This code also provides….. “Telemetry/communication system & Data Acquisition System shall also be provided for transfer of information to the concerned SLDC and RLDC.”
Regulation for Real-time RE Data Communication

## Slide 22
Type of Communication | Radio Modem | GSM / GPRS | Lease Line | Internet Lease Line | Total
Nos. of Wind station (Main) | 6 | 5 | 34 | 27 | 72
Nos. of Wind station (Standby) | - | 51 | 15 | - | 72
Nos. of Solar Plant | 76 | 8 | 2 | - | 86
Real-time RE Generation Data Communication
Real-time generation data of all RE generators located in Gujarat State, which are connected to STU substation are communicated through various communications system. Data connectivity between RE Station injection point (at 66 KV level & above) and STU End Sub-Station with mix of available Technologies are as below:
In caser further extended communication required from STU S/S to Sub SLDC, PLCC, Fiber Optic, Lease Line etc are being utilised.

## Slide 23
Type of Communication | Radio Modem | GSM / GPRS | Lease Line | PLCC | Total
Nos. of Wind Pooling station | 10 | 44 | 6 | 8 | 68
Nos. of Solar Plant | 51 | 30 | 3 | - | 81
Real-time RE Generation Data Communication
Real-time generation data of all RE generators located in Gujarat State, which are connected to STU substation are communicated through mix of communications technology.
Data connectivity between RE Station injection point (at 66 KV level & above) and STU End Sub-Station with mix of available Technologies are as below:

## Slide 24
Real-time RE Data Communication
Detail Communication of Data between SLDC and Sub SLDC. |  |  |  |  | 
From | To | Connection | Earlier (Main) | Earlier (Back up) | New Scada
SLDC, Vadodara | Sub LDC Jambuva | P 2 P | 2 Mbps Fiber | 64 Kbps Leas Line | 4 Mbps Fiber
SLDC, Vadodara | Sub LDC Jetpur | P 2 P | 2 Mbps Fiber | 64 Kbps Leas Line | 4 Mbps Fiber
SLDC, Vadodara | Sub LDC Gandhinagar | P 2 P | 2 Mbps Fiber | 64 Kbps Leas Line | 4 Mbps Fiber
SLDC, Vadodara | Back Up SLDC Gandhinagar | P 2 P |  |  | 10 Mbps Fiber
Sub LDC Jetpur | Back Up SLDC Gandhinagar | P 2 P |  |  | 4 Mbps Fiber
Sub LDC Jambuva | Back Up SLDC Gandhinagar | P 2 P |  |  | 4 Mbps Fiber
BSNL + redundancy of Airtel

## Slide 25
    Real-time Data Communication Charges

## Slide 26
Market for Real-time Data Communication
RTU Vendor List:
M/s Honeywell Automation India Limited,
M/s Siemens Limited,
M/s Applitech Infotech,
M/s Chemtrols Industries Limited,
M/s ALSTOM T&D India Ltd.
Radio Link Supplier:
M/s Kirti Telenet Pvt. Ltd.
M/s Midaas Telesoft Private Limited,
M/s Sheetal Wireless Technologies Pvt Ltd
M/s.Process & Machines Automation Systems

## Slide 27
Real-time Data Communication Charges
Approximate Charges for communication
RTU: 4,95,000 RS.
Radio link: 3,00,000 RS. (Further, charges depends on repeater)
Lease line: 20,000 RS. installation process + 60,000 RS. Annual maintenance charge
GSM/GPRS: 20,000 RS. Annual maintenance charge

## Slide 28
Real-time Data Communication Charges
Onetime Charges:
Data base development charges: 40,300 RS.
Charges for define analog & digital database and integration of the same at Front End Processor (FEP)
IEC protocol port charges: 50,000 RS for main & 50,000 RS for Standby port.
Charges for link communication from RTU, modem, switch, router to port
Rental Charges: 13,104 RS / annual
Providing space and supply for RTU & communication infrastructure at STU S/S & Sub SLDC

## Slide 29
Thanking you !!!