## Slide 1
Power System Operation Corporation Ltd.
“Furnishing Real Time/Daily Renewable Energy Generation Data” meeting
at Jaipur on 4th May 2018
WRLDC Presentation
Notes: 1

## Slide 2
Type Wise Capacity
Total Installed Capacity – 341 GW
Renewable:
66 GW
Peak Demand met:
160 GW
Indian Power Scenario
Chart: Fuel wise Installed capacity (as on 31.03.2018)
| Coal | Gas | Diesel | Nuclear | Hydro | Wind | Solar | Bio power | Small Hydro
India | 197171.5 | 24897.46 | 837.63 | 6780 | 45293.42 | 32957.86 | 19584.18 | 8527.88 | 4476.66

## Slide 3
Type Wise Capacity
Total Installed Capacity – 110 GW
Wind-RE
12789 MW
Peak Demand met:
52276 MW
Western Region Power Scenario
Peak Energy Met
1180 MUs
Max Wind Gen.
7885 MW
Max Gen 58786 MW
Max Wind Energy
Gen: 169 MUs
Solar-RE
4171 MW
Max Solar Gen.
3103 MW
Max Solar Energy
Gen: 21 MUs
Max RE (Wind+Solar) Gen. 9031 MW
Chart: Western Region Fuel wise Installed capacity (as on 31.03.2018)
Chart: Western Region Fuel wise Installed capacity as on April’18
| Coal | Gas | Diesel | Nuclear | Hydro | Wind | Solar | Hydro/Bio
WR | 70608.62 | 10806.49 | 0 | 1840 | 7447.5 | 12789 | 4171 | 2726.05

## Slide 4
Wind Power Capacity in WR (in MW) |  |  |  | 
Constituents | As on April’18 (A) | Target by Year 2022 (B) | Balance (C=B-A) | % balance target capacity
Gujarat | 5575 | 8800 | 3225 | 37
Maharashtra | 4776 | 7600 | 2824 | 37
Madhya Pradesh | 2438 | 6200 | 3762 | 61
Total | 12789 | 22600 | 9811 | 43
Wind Generation Targets by 2022 in Western Region
Chart: Target for Wind capacity addition by 2022
| Gujarat | Maharashtra | Madhya Pradesh | Total WR
As on Apr'18 (A) | 5575 | 4775.51 | 2438 | 12788.51
Target by Year 2022 (B) | 8800 | 7600 | 6200 | 22600

## Slide 5
Solar Generation Targets by 2022 in Western Region:
Chart: Target for Solar Installed Capacity by 2022
| Gujarat | Maharashtra | Madhya Pradesh | Chhattisgarh | Daman & Diu | DNH | Goa | WR
As on Apr'18 (A) | 1493.31 | 1305 | 1282.5 | 76 | 10 | 4.1 | 4170.91
Target by Year 2022 (B) | 8020 | 11926 | 5675 | 1783 | 199 | 449 | 358 | 28410

## Slide 6
 | 2015-16 | 2016-17 | 2017-18 | Anticipated in 2018-19
Solar Installed Capacity in MW | 2266 | 2526 | 3925 | 10046
Max Solar Gen in MW | 1643 | 1807 | 2992 | 7658
 | 2015-16 | 2016-17 | 2017-18 | Anticipated in 2018-19
Wind Installed Capacity in MW | 9797 | 12515 | 12724 | 15193
Max Wind Gen in MW | 5318 | 6431 | 7885 | 9415
Anticipated Highest Wind & Solar Generation in 2018-19
Note: Anticipation is calculated by distributing the target capacity(2022 Plan) over the year.

## Slide 7
Average WR Wind Gen in July’17 - 114 Mus
Highest Wind generation |  |  |  |  | 
State | Gen (in MW) | Date | Time | Demand (in MW) on Max Wind Gen day | Penetration (%)w.r.t. demand
Gujarat | 3763 | 05.07.2017 | 18:00 | 10720 | 35.1
MP | 1779 | 25.07.2017 | 16:00 | 5124 | 34.7
Maharashtra | 3002 | 24.07.2017 | 12:00 | 16607 | 18.1
WR | 7885 | 04.07.2017 | 11:00 | 37722 | 20.9
Full day total WR Wind > 5500 MW
Growth in Max Wind Generation (MW) : 23 %
Notes: Good wind generation in mid January

## Slide 8
Installed Capacity-12777 MW
Highest Ever Generation - 7885 MW on 4th July’17
CUF -63%
WR Wind Generation April’17-March’18

## Slide 9
Jul
Highest wind Generation in Western Region achieved 7885 MW on 4th July’17

## Slide 10
Max Wind Gen- 169 Mus on 25.07.17
Guj- 67 Mus
Mah- 63 Mus
MP- 39 Mus
Growth in Max Wind Generation (MUs) : 20.7%

## Slide 11
Hourly Solar generation in MW for 2017-18
Average WR Solar Gen -13 Mus

## Slide 12
So Far Highest RES(Wind+Solar) Generation is also achieved in the month of July’17
9031 MW
on 4th July’2017 at 11Hrs
So Far Highest Wind Generation is achieved in the month of July’17
7885 MW
on 4th July’2017 at 11Hrs
So Far Highest Solar Generation is also achieved in the month of Apr’18
3103 MW
on 24th Apr 2018 at 12 Hrs

## Slide 14
Telemetry Issues

## Slide 15: Telemetry of Wind Renewable Energy Sources in WR
Visibility/Observability of Wind RES at WRLDC: 95.10%
Maharashtra Wind Data Integrated through ICCP at WRLDC is 93%, but the real time generation data availability is very less due to communication problems.
Real time visibility of Masharashtra wind on reliable communication to be expedited.
Any capacity addition shall be informed to RLDC for data integration through ICCP.
State/Region | Installed Capacity | Telemetered | % of Visibility/Observability at SLDC/WRLDC
Gujarat | 5575 | 5339 | 95.77
Maharashtra | 4776 | 4460 | 93.3%
Madhya Pradesh | 2438 | 2364 | 97
Chhattisgarh | 0 | 0 | -
Daman & Diu | 0 | 0 | -
DNH | 0 | 0 | -
WR | 12789 | 12163 | 95.10

## Slide 16: Telemetry of Solar Renewable Energy Sources in WR
Visibility/Observability of Solar RES at WRLDC: 97.89%
WR Solar RES Installed Capacity: 4171 MW
Maharashtra Solar Data Integrated through ICCP at WRLDC is 100%.
Any capacity addition shall be informed to RLDC for data integration through ICCP.
State/Region | Installed Capacity | Telemetered Capacity | % of Visibility/Observability at SLDC/WRLDC
Gujarat | 1493 | 1420 | 95.11
Maharashtra | 1305 | 1305 | 100
Madhya Pradesh | 1283 | 1282 | 100
Chhattisgarh | 76 | 66 | 86.84
Daman & Diu | 10 | 10 | 100
DNH | 4 | 0 | 0
WR | 4171 | 4083 | 97.89

## Slide 17
Sr. No. | Solar Devloper | MW Capacity
1 | Bhageria Ind. | 30
2 | Enrich Karasgi | 25
3 | Enrich Mandrup | 25
4 | Essel MP | 20
5 | Fermi Solar | 80
6 | Firestone | 5.25
7 | Fourth Dimn. | 30
8 | Gale Saltek | 50
9 | Giriraj (Varkute Malwadi) | 100
10 | Greenraj Solar | 100
11 | Jain Irrigation | 8.5
12 | JBM Solar | 100
13 | Jindal Polyfilms | 2.5
14 | Kiran Renew | 4.6
15 | Kirloskar Oil (Kagal) | 5.5
16 | Krishna Windfarm | 10
17 | LREHL Renewables | 50
18 | Morries Energy | 8
19 | Parampujya Solar | 20
20 | RYB Solar | 10
21 | Sakri Solar | 125
22 | Sepset Solar | 40
23 | Sharda Const. | 10
24 | Shirsuphal Solar | 36
25 | SolarEdge Mahtargaon | 80
26 | SolarEdge Muktaingar | 50
27 | Sukhbir Agro | 30
28 | Sunbless Solar | 30
29 | Talettutayi Solar | 50
30 | Tata Palaswadi | 55
31 | Vaibhav Solar | 10
32 | Varrac Engg. | 5
33 | NVR Mahasolar | 50
34 | Visa Tornado (Saltek) | 20
35 | Vishwaj Energy | 10
36 | Welpun Energy | 20
Total Capacity |  | 1305.35
Status of renewable generation visibility as on 12-04-2018 |  |  |  |  |  | 
State | Wind |  |  | Solar |  | 
 | Installed capacity | Telemetered capacity | % Telemetry availability | Installed capacity | Telemetered capacity | % Telemetry availability
Maharashtra | 4775.51 | 4460 | 93.39% | 1305.35 | 1305.35 | 100.00%
Sr.No. | Wind Developer | MW Capacity |  | Sr.No. | Wind Developer | MW Capacity
1 | Aditya Engg (Bhud) | 30 |  | 37 | Suzlon (Kundalapur) | 8.7
2 | Amrik (Khaprale) | 18.3 |  | 38 | Suzlon (Malharpeth) | 46.6
3 | Gamesa (Bhendewadi) | 24.65 |  | 39 | Suzlon (Mendigiri) | 121.8
4 | Gamesa (Kirvere) | 47.6 |  | 40 | Suzlon (Nandurbar) | 40
5 | Gamesa (Mendigiri) | 39.1 |  | 41 | Suzlon (Nigde) | 94.8
6 | Gamesa (Vaspeth) | 198.7 |  | 42 | Suzlon (Pandurli) | 9
7 | Giriraj (Ambheri) | 16 |  | 43 | Suzlon (Parali) | 11.41
8 | Giriraj (Kadegaon) | 14.8 |  | 44 | Suzlon (Ranala) | 11.21
9 | Giriraj (Sanmadi) | 10 |  | 45 | Suzlon (Sadawaghapr) | 117.9
10 | ITC (Bhud) | 6 |  | 46 | Suzlon (Savlaj) | 23.75
11 | ITC (Chakla) | 6.3 |  | 47 | Suzlon (Shirshi) | 8.4
12 | Krishna Power (Aundh) | 8.4 |  | 48 | Suzlon (Supa) | 35
13 | Malpani (Nigde) | 24 |  | 49 | Suzlon (Undale) | 6
14 | Maruti Wind (Bhud) | 250 |  | 50 | Suzlon (Vankuswade) | 186.4
15 | Maruti Wind (Shedyal) | 250 |  | 51 | Suzlon (Vita) | 10.5
16 | Panama (Nerle) | 12 |  | 52 | Suzlon (Walve) | 168.1
17 | Panama-2 (Beed) | 80 |  | 53 | Suzlon(Ghatnandare) | 226.15
18 | Regen (Hiwarwadi) | 141 |  | 54 | T S Wind (Aundh) | 32.8
19 | Regen (Mayani) | 25.5 |  | 55 | TS Wind (Alephata) | 29.7
20 | Regen Pwr (Sawargaon) | 31.5 |  | 56 | TS Wind (Medha) | 7.2
21 | Renew Pwr (Khandke) | 28 |  | 57 | TS Wind (Shirala) | 42
22 | Renew Wind (Aundh) | 28 |  | 58 | TS Wind (Wai) | 20.1
23 | RWPPL (Palsi) | 65.5 |  | 59 | Valsang (Sangli) | 102
24 | Sanjana Power (Satara) | 4 |  | 60 | Vestas (Bothe) | 80
25 | Serum Inst (Jath) | 37.5 |  | 61 | Vestas (Karve) | 42.9
26 | Serum Inst (Sakri) | 33.6 |  | 62 | Vestas (Sakri) | 52.95
27 | Shah Devp (Khandke) | 7.2 |  | 63 | Vestas (Shirala) | 37.95
28 | Shah Devp (Koregaon) | 12 |  | 64 | Victory Windfarm (Jamkhed) | 9
29 | Shiva Renewables (Jath) | 14 |  | 65 | Vish Wind(Khandke) | 200
30 | ShriRam (Kokrale) |  |  | 66 | Windworld (Andralake) | 125
31 | Suyog Urja (Anjanwadi) | 50 |  | 67 | Windworld (Bhambarwadi) | 50
32 | Suzlon (Bhoyre Pathar) | 7.5 |  | 68 | Windworld (Chavneshwar) | 100
33 | Suzlon (Gangapur) | 236.25 |  | 69 | Windworld (Karvekurdh) | 
34 | Suzlon (Jamde) | 328.35 |  | 70 | Windworld (Khanapur) | 100
35 | Suzlon (Jath) | 37.8 |  | 71 | Windworld (Khandke) | 100
36 | Suzlon (Kedgaon) | 22 |  | 72 | Windworld (Panchapatta) | 62.4
 |  | 2145.55 |  | 73 | Windworld (Varekarwadi) | 
Total Capacity |  |  |  |  |  | 2319.7

## Slide 18
Comparison of Maharashtra Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: Maha. Wind Gen. SCADA Vs State data_02-05-2018
Wind_SCADA | 598.4096 | 571.0097 | 566.3191 | 541.7244 | 507.5859 | 509.6597 | 438.3884 | 320.1618 | 254.054 | 253.8988 | 130.1542 | 129.4212 | 176.8658 | 199.9823 | 203.597 | 219.4419 | 260.6664 | 446.1079 | 562.8713 | 608.7631 | 663.5259 | 688.0371 | 673.5064 | 640.9545
Wind_State | 1401 | 1422 | 1304 | 1316 | 1274 | 1146 | 1130 | 712 | 666 | 423 | 410 | 388 | 514 | 638 | 720 | 914 | 1202 | 1568 | 1678 | 1538 | 1456 | 1406 | 1285 | 1191
Chart: Maha. Solar Gen. SCADA Vs State data 02-05-2018
Solar_SCADA | 0 | 0 | 0 | 0 | 0 | 0 | 67.9735 | 197.8249 | 394.9197 | 576.5404 | 672.7644 | 743.8281 | 703.3574 | 674.1314 | 662.4347 | 538.1225 | 364.8586 | 195.1662 | 48 | 0 | 0 | 0 | 0 | 0
Solar_State | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 208 | 429 | 647 | 785 | 848 | 876 | 832 | 715 | 535 | 377 | 193 | 13 | 0 | 0 | 0 | 0 | 0

## Slide 19
Chart: MAH. State Wind Vs MAH.SCADA Wind for 28-03-2018
Mah. State Wind | 700 | 609 | 584 | 551 | 559 | 549 | 433 | 307 | 196 | 214 | 199 | 191 | 183 | 285 | 365 | 376 | 508 | 507 | 618 | 624 | 716 | 841 | 800 | 774
Mah. SCADA Wind | 309.0632 | 303.4087 | 300.0932 | 291.8708 | 272.9425 | 257.2915 | 255.05 | 254.1243 | 243.3097 | 250.1605 | 266.2458 | 262.774 | 252.6778 | 235.6827 | 222.7758 | 222.8388 | 213.9198 | 210.418 | 250.3855 | 307.5942 | 303.4742 | 413.3227 | 466.9923 | 438.957
Comparison of Maharashtra Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: MAH. State Solar Vs MAH. SCADA Solar for 28-03-2018
Mah. State Solar | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 117 | 327 | 515 | 603 | 676 | 660 | 664 | 579 | 448 | 301 | 110 | 2 | 0 | 0 | 0 | 0 | 0
Mah. SCADA Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0.372 | 17.4403 | 44.5875 | 79.4 | 92.6232 | 94.89 | 97.928 | 93.9992 | 84.3063 | 73.3847 | 49.0635 | 8.3693 | 0.94483 | -0.236 | -0.17517 | -0.152 | -0.12517 | -0.12067
Hour

## Slide 20
Chart: Gujarat Wind Gen. SCADA Vs State data-02-05-2018
Wind_SCADA | 1494.87 | 1424.1887 | 1247.3857 | 1074.2297 | 962.2627 | 841.6783 | 798.312 | 759.1588 | 896.7287 | 952.0205 | 1088.4725 | 1323.0162 | 1628.2775 | 1943.748 | 2168.2632 | 2355.8125 | 2456.8828 | 2621.5127 | 2595.9933 | 2313.3015 | 2116.4145 | 2129.8307 | 1951.2663 | 1911.9252
Wind_State | 1519 | 1427 | 1303 | 1129 | 1051 | 916 | 776 | 771 | 896 | 1005 | 1081 | 1369 | 1635 | 1985 | 2195 | 2410 | 2543 | 2697 | 2640 | 2346 | 2162 | 2198 | 2002 | 1986
Comparison of Gujarat Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: Gujarat Solar Gen. SCADA Vs State data_02-05-2018
Solar_SCADA | 0 | 0 | 0 | 0 | 0 | 0 | 13.2688 | 147.9517 | 379.7845 | 601.158 | 763.3995 | 861.8862 | 893.3013 | 873.188 | 806.7985 | 671.6765 | 479.9958 | 245.7672 | 62.1708 | 0 | 0 | 0 | 0 | 0
Solar_State | 0 | 0 | 0 | 0 | 0 | 0 | 106.87 | 314.04 | 564.33 | 787.86 | 923.04 | 982.76 | 1011.2 | 954.04 | 810.49 | 622.96 | 378.18 | 140.29 | 24.04 | 1.03 | 0 | 0 | 0 | 0

## Slide 21
Comparison of Gujarat Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: Gujrat State Wind Vs Gujarat SCADA Wind for 28-03-2018
GUJ. STATE Wind | 1288 | 1328 | 1401 | 1308 | 1149 | 1136 | 892 | 718 | 387 | 157 | 210 | 220 | 343 | 352 | 435 | 588 | 787 | 964 | 1040 | 1220 | 1216 | 1001 | 820 | 757
GUJ. SCADA Wind | 1243.1295 | 1263.3937 | 1302.6383 | 1203.2122 | 1088.5648 | 1090.3003 | 948.0797 | 718.6782 | 438.6053 | 199.769 | 198.8287 | 274.0702 | 337.491 | 374.9803 | 469.4783 | 616.0323 | 778.8752 | 903.3847 | 981.109 | 1182.6197 | 1266.8538 | 1020.1367 | 801.2125 | 744.1742
Chart: Guj. State Solar Vs Guj SCADA Solar for 28-03-2018
Guj. State Solar | 0 | 0 | 0 | 0 | 0 | 0 | 58.68 | 248.31 | 527.43 | 765.22 | 919.46 | 997.45 | 1024 | 958.55 | 859.31 | 658.38 | 420.34 | 156.26 | 20.05 | 0 | 0 | 0 | 0 | 0
Guj. SCADA Solar | 0.211 | 0.2 | 0.20017 | 0.20067 | 0.21967 | 0.21967 | 3.43 | 84.9363 | 355.5263 | 630.6433 | 832.5663 | 949.8707 | 993.837 | 979.9377 | 902.5657 | 770.7492 | 555.3083 | 288.7843 | 47.5498 | 2.0158 | -0.084333 | -0.086667 | -0.075833 | -0.06
Hour
Hour

## Slide 22
Comparison of Madhya Pradesh Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: MP Solar Gen. SCADA Vs State data_02-05-2018
Solar_SCADA | 0 | 0 | 0 | 0 | 0 | -0.17367 | 36.8372 | 227.6265 | 505.957 | 701.9805 | 834.8613 | 925.8278 | 947.5995 | 927.823 | 819.567 | 691.4548 | 460.174 | 200.0127 | 30.3618 | 0 | 0 | 0 | 0 | 0
Solar_State | 0 | 0 | 0 | 0 | 0 | 0.06 | 104.28 | 399.62 | 600.76 | 837.27 | 967.72 | 1010.52 | 988.7 | 849.4 | 622.99 | 541.44 | 329.1 | 71.68 | 0.06 | 0 | 0 | 0 | 0 | 0
Chart: MP Wind Gen. SCADA Vs State data_02-05-2018
Wind_SCADA | 1516.573 | 1393.568 | 1320.245 | 1178.468 | 1080.9168 | 1015.918 | 845.7642 | 548.2268 | 389.5708 | 395.57 | 500.6933 | 617.1733 | 624.8317 | 637.9067 | 664.7515 | 720.9392 | 794.9913 | 980.6828 | 1185.449 | 1201.6687 | 1210.0318 | 1304.7202 | 1275.3638 | 1275.0462
Wind_State | 1376.2 | 1314.86 | 1195.39 | 1111.2 | 1011.68 | 938.25 | 677.75 | 385.94 | 336.88 | 409.01 | 561.56 | 601.62 | 582.32 | 612.39 | 650.61 | 691.68 | 861.98 | 1034.65 | 1203.65 | 1158.39 | 1246.23 | 1286.6 | 1215.94 | 1276.05

## Slide 23
Comparison of Madhya Pradesh Wind & Solar Generation Vs Telemetry Data on a typical day
Chart: MP State Solar Vs MP SCADA Solar for 28-03-2018
MP State Solar | 0 | 0 | 0 | 0 | 0 | 0 | 58.59 | 351.93 | 648.02 | 867.72 | 987.38 | 1048.77 | 1049.04 | 987.01 | 821.33 | 651.58 | 351.27 | 63.37 | 0 | 0 | 0 | 0 | 0 | 0
MP SCADA Solar | 0 | 0 | 0 | 0 | 0 | 0 | 13.4338 | 185.2265 | 508.5053 | 761.6495 | 939.733 | 1028.5212 | 1054.6722 | 1025.5025 | 917.3032 | 749.6028 | 532.3435 | 210.2237 | 31.0567 | -1.804 | -1.805 | -1.8813 | -0.7135 | 0
Chart: MP State Wind Vs MP SCADA Wind for 28-03-2018
MP STATE WIND | 1148.91 | 1009.54 | 933.35 | 891.25 | 853.16 | 818.66 | 702.47 | 558.65 | 234.01 | 292.26 | 221.02 | 127.79 | 110.42 | 154.34 | 149.82 | 141.57 | 148.15 | 128.23 | 157.84 | 166.71 | 173.85 | 173.65 | 303.15 | 379.77
MP SCADA WIND | 1290.024 | 1123.4027 | 1040.1522 | 943.4215 | 918.1602 | 870.6777 | 781.4312 | 689.2445 | 404.2262 | 260.3183 | 272.2707 | 197.0922 | 135.8477 | 151.647 | 179.9688 | 145.7422 | 156.9617 | 139.6957 | 142.4373 | 162.6792 | 188.1118 | 194.6342 | 215.3582 | 350.3153
Hour
Hour

## Slide 24
Chart: WR Wind Gen SCADA Vs State data_02-05-2018
Wind_SCADA | 3609.8526 | 3388.7663 | 3133.9498 | 2794.4221 | 2550.7654 | 2367.256 | 2082.4646 | 1627.5474 | 1540.3535 | 1601.4893 | 1719.3201 | 2069.6107 | 2429.975 | 2781.637 | 3036.6117 | 3296.1936 | 3512.5406 | 4048.3034 | 4344.3136 | 4123.7333 | 3989.9723 | 4122.588 | 3900.1366 | 3827.9258
Wind_State | 4296.2 | 4163.86 | 3802.39 | 3556.2 | 3336.68 | 3000.25 | 2583.75 | 1868.94 | 1898.88 | 1837.01 | 2052.56 | 2358.62 | 2731.32 | 3235.39 | 3565.61 | 4015.68 | 4606.98 | 5299.65 | 5521.65 | 5042.39 | 4864.23 | 4890.6 | 4502.94 | 4453.05
Chart: WR Solar Gen SCADA Vs State data_02-05-2018
Solar_SCADA | 0 | 0 | 0 | 0 | 0 | 0 | 122.135 | 586.623 | 1307.4823 | 1915.0354 | 2313.5783 | 2576.9845 | 2589.7092 | 2517.5263 | 2324.8539 | 1927.8235 | 1318.3679 | 644.4775 | 140.5327 | 0 | 0 | 0 | 0 | 0
Solar_State | 0 | 0 | 0 | 0 | 0 | 5.06 | 289.15 | 994.66 | 1699.09 | 2404.13 | 2819.76 | 2987.28 | 3015.9 | 2758.44 | 2246.48 | 1763.4 | 1109.28 | 408.97 | 37.1 | 1.03 | 0 | 0 | 0 | 0
Comparison of Western Region Wind & Solar Generation Vs Telemetry Data on a typical day

## Slide 25
FORECASTING OF RENEWABLE ENERGY IN
WESTERN REGION

## Slide 26
Error Summary for 01-05-2018
Note-
1-Errors are Normalized w.r.t. Wind Installed Capacity.
2- Maharashtra Forecast is prepared for 2595MW capacity out of 4769MW (total Wind Cap of Maharashtra). Therefore the error is normalized w.r.t. 2595MW capacity.
 | Mean Absolute Percentage Error(MAPE) |  |  |  |  |  |  | 
 | R0(Day Ahead) |  |  |  | R16(Final Forecast) |  |  | 
 | Mah | Guj | MP | WR | Mah | Guj | MP | WR
Error(%) | 4 | 9 | 16 | 5 | 5 | 3 | 6 | 3
 | Root Mean Square Error(RMSE) |  |  |  |  |  |  | 
 | R0(Day Ahead) |  |  |  | R16(Final Forecast) |  |  | 
 | Mah | Guj | MP | WR | Mah | Guj | MP | WR
Error(%) | 6 | 11 | 18 | 6 | 6 | 4 | 7 | 3

## Slide 32
VARIABILITY OF WIND GENERATION:
Over Drawl of MP of ~900 MW
Frequency: ~49.7 Hz
Forecasting is required :
  To schedule RES as per forecasting
  To fine tune schedules as per real time forecasting
  Prevent system contingencies due to sudden withdrawal of wind
  Plan power generation to meet the demand

## Slide 33: VARIABILITY OF WIND GENERATION:
For real time Grid Operation it is must to have
Real-time telemetry from RES in the State
Forecast of RES and demand by the SLDCs
Reduction of WR Wind from 6000 MW to 3000 MW

## Slide 34: IEGC Clauses for Telemetry for RES
Special requirements for Solar/ wind generators

## Slide 35: IEGC Regulation 5.2 (u)
System operator (SLDC/ RLDC) shall make all efforts to evacuate the available solar and wind power and treat as a must-run station. However, System operator may instruct the solar /wind generator to back down generation on consideration of grid security or safety of any equipment or personnel is endangered and Solar/ wind generator shall comply with the same. For this, Data Acquisition System facility shall be provided for transfer of information to concerned SLDC and RLDC.
  (i) SLDC/RLDC may direct a wind farm to curtail its VAr drawl/injection in case the security of grid or safety of any equipment or personnel is endangered.
  (ii) During the wind generator start-up, the wind generator shall ensure that the reactive power drawl (inrush currents in case of induction generators) shall not affect the grid performance. "

## Slide 36: IEGC Regulation 6.2
This code also provides the methodology for re-scheduling of wind and solar energy generators which are regional entities, on one and half hourly basis and the methodology of handling deviations of such wind and solar energy generators. Appropriate meters shall be provided for accounting of charges for deviation under DSM Regulations. Telemetry/communication system & Data Acquisition System shall also be provided for transfer of information to the concerned SLDC and RLDC.”

## Slide 37: IEGC Clauses for Forecasting of RES
As per IEGC 5.3(g)
“The SLDC shall take into account the Wind Energy forecasting to meet the active and reactive power requirement.”
And as per IEGC 6.5.23(ii)
Forecasting shall be done by wind and solar generators which are regional entities as well as the concerned RLDC. The concerned RLDC may engage forecasting agency(ies) and prepare a schedule for such generating stations. The forecast by the concerned RLDC shall be with the objective of ensuring secure grid operation. The forecast by the wind and solar generator shall be generator centric. The wind and solar generators which are regional entities will have the option of accepting the concerned RLDC’s forecast for preparing its schedule or provide the concerned RLDC with a schedule based on its own forecast. Any commercial impact on account of deviation from schedule based on the forecast chosen by the wind and solar generator shall be borne by it.”

## Slide 38: WR RE achievements
 | Wind | YoY position | Solar | YoY position
Installed Capacity | 12777 MW | 10 % | 3925 MW | 72 %
Max Power | 7885 MW 04-Jul-17 | 23 % | 2992 MW 30-Mar-18 | 66 %
% of WR demand met | 23% |  |  | 
Max Energy | 169 MU 25-Jul-17 | 21 % | 22 MU 31-Mar-18 | 70 %
Generation from the installed RES in WR could be absorbed without curtailment in Western Region
As on 31-Mar-18

## Slide 39: COMPLIANCE OF CEA STANDARDS W.R.T. TO LOW VOLTAGE RIDE THROUGH CAPABILITY (LVRT)

## Slide 40: Regulation Part II (B2) (3) of the CEA (Technical Standards for Connectivity to the Grid)
Notified on 15th October 2013 mandates as under:
  “B2. For generating station getting connected on or after completion of 6 months from date of publication of these Regulations in the Official Gazette.
  ….
  (3) Wind generating stations connected at voltage level of 66 kV and above shall remain connected to the grid when the voltage at the interconnection point on any or all phases dips upto the levels depicted by the thick lines in the curve

## Slide 41: CERC Order on LVRT
Hon’ble Central Electricity Regulatory Commission vide its order dated 05.01.16 in Petition No.420/MP/2014 mandated that
“………We are of the view that LVRT should be implemented for all wind turbines commissioned before 15.4.2014 and connected to voltage level of 66 kV and above except for Stall Type WTGs, which are not technically feasible to be retrofitted with LVRT. However, keeping in view the suggestions of IWTMA, we are of the view that presently LVRT should be implemented for all wind turbines (except Stall Types) commissioned before 15.04.2014 having installed capacity equal to or more than 500 KW.”

## Slide 42: LVRT Status Western Region:
Constituent | Total Installed Wind Power Capacity (MW) | Exempted Capacity (MW) | Information received for (MW) | LVRT Complied capacity out of information received (MW)
Gujarat | 5574 | Not Available | 2617 | 471
Madhyapradesh | 2428 | Not Available | 1205 | 1205
Maharashtra | 4775 | Not Available | Nil | Nil

## Slide 43: LVRT Status:
Partial data of Gujarat and Madhyapradesh is provided.
No status received from Maharashtra SLDC.
All SLDCs at requested to provide data of LVRT compliance/exemption to WRPC and WRLDC.
All SLDCs shall inform the methodology adopted for ensuring compliance of LVRT regulations.

## Slide 44
Location | Developer | Pooling Station | Turbine make | Turbine type | Turbine Capacity | If turbine commissioned before 15.04.2014, Expected date of completion of retrofitting | If turbine commissioned after 15.04.2014 whether compliant to LVRT (Yes/No)
… | … | … | … | … | … | … | …
… | … | … | … | … | … | … | …
Format for Information of Wind Turbines and LVRT compliance

## Slide 45: Status of Forecasting of RES in Western Region:
State/Region | Status of Forecasting
Gujarat | Wind Forecasting is being done and shared with WRLDC.
Maharashtra | Not Done
Madhya Pradesh | Wind and Solar Forecasting is done and shared with WRLDC.
Chhattisgarh | Not Done
Daman & Diu | Not Done
DNH | Not Done
WRLDC | Pilot Project for forecasting of Maharashtra RES undertaken and is being done for around 50% of installed capacity.

## Slide 46: FORECASTING OF RENEWABLE ENERGY
SLDCs shall forecast wind and solar RES for better management and integration of RES.

## Slide 47: Voltage Regulation by RES:
Most of the wind RES are connected on lower voltage level the grid. During the high wind season, the demand at lower voltage level is being met by wind RES resulting high voltages on many nodes of south Maharashtra and Madhyapradesh.
The capability of reactive power drawl/injection by wind RES can be harnessed to support the grid for Voltage Management.

## Slide 48
Chart: Karad Substation Voltage Variation Vs Wind Generation
1. High Voltage Scenerio is observed at Sub -station situated in areas with high density of wind farms .
2. Voltage remained above 420 KV for 60-70% of the time at Karad and Dhule sub-station.
3. As the wind generation picks up during high wind season, overvoltage scenario observed in the sub-stations.
4. Reactive power injection/drawl capability of wind turbines can be used for voltage management in such scenarios.
High Voltage Scenario due to Wind:

## Slide 49: High Voltage Scenario due to Wind:
Chart: Dhule Substation Voltage Variation Vs Wind Generation

## Slide 50: Voltage Regulation by RES: Rates for VAR injection

## Slide 51: Voltage Regulation by RES:
As per MoM of 2nd REIF it was suggested that reactive charges are to be made voltage dependent in line with the ISTS reactive energy settlement instead linking it to power factor.
It was decided that the above suggestion could be forwarded to SERCs, CEA and CERC.
Members may inform any action taken in this regard.

## Slide 52
INTEGRATION OF NEW ISTS CONNECTED RENEWABLE ENERGY SOURCES

## Slide 53: NEW RES YET TO BE CONNECTED TO ISTS
Sl.No. | Organization Name | Generating Station Location | Capacity in MW | Date from connectivity reqd | Granted connectivity for
1 | WIND WORLD (INDIA) LTD MUMBAI | Bhuj | 500 | 31-Mar-17 | 500
2 | INOX WIND INFRASTRUCTURE SERVICES LIMITED | KACHCHH | 500 | 30-Jul-17 | 500
3 |  | Kachchh | 500 | 01-Jul-17 | 500
4 | GAMESA RENEWABLE PVT LTD | Bhuj | 100 | 31-Mar-17 | 100
5 |  | DHAR | 218 | 31-Mar-17 | Accepted and under process
6 | KP ENERGY LIMITED | Kutch | 400 | 25-May-17 | Accepted and under process
7 |  |  |  |  | 
 |  | Kutch | 400 | 25-May-17 | Accepted and under process
8 |  |  |  |  | 
 |  | Kutch | 400 | 25-May-17 | Awaiting for Acceptance
9 |  | Kutch | 400 | 25-May-17 | Awaiting for Acceptance
10 | GUJARAT POWER CORPORATION LIMITED | BANASKANTHA | 700 | 31-Dec-17 | 700
11 | RENEW POWER VENTURES PRIVATE LIMITED | Kutch | 400 | 15-Dec-17 | 400
12 | REWA ULTRA MEGA SOLAR LIMITED | Rewa | 500 | 31-Mar-17 | 750
13 | KADAPA WIND FARMS PRIVATE LIMITED | BHUJ | 100 | 31-Mar-17 | Accepted and under process
14 | SRI MARUTI WIND PARK (MENDIGIRI) PRIVATE LIMITED | Kucth District | 400 | 20-Jun-17 | Awaiting for Acceptance
 | Total Capacity to be connected by Dec.’17 |  | 5518 |  | 

## Slide 54: Procedure for Connectivity:
Hon’ble CERC have issued “ Procedure for Implementation of Framework on Forecasting, Scheduling and imbalance Handling for Renewable Energy Generating Stations including Power Parks based on Wind and Solar at Inter State Level.”
The same is available on CERC website at http://www.cercind.gov.in/2017/regulation/pro.pdf
All new ISTS connecting RES shall submit data in prescribed formats to WRLDC for First Time Charging (FTC), as approved by CERC in above procedure.

## Slide 55: Data requisite for Grid Connectivity:
For First Time Charging (FTC), following data shall be submitted to WRLDC for ISTS connecting RES.
For Wind RES:
Static data of the wind turbines and wind parks as mentioned in framework ( covers 70 points including details of turbine, blade, generator, transformer, performance parameters etc.)
First Time Charging Formats A to C ( includes details of T/L, transformer, bays, SLD, communication conformity, energy meter conformity etc.)
Undertaking by RE/Lead/Principal regarding discharging all operational and commercial responsibilities on behalf of generating stations as per the prevalent CERC Regulations.
Copy of application for connectivity which was submitted to CTU.
5. Undertaking to indemnify, defend and save the SLDCs/RLDCs harmless from any and all damages, losses including commercial losses.

## Slide 56: Data requisite for Grid Connectivity:
For Solar RES:
Static data of the solar PV modules and Solar Parks as mentioned in framework ( covers 16 points including details of PV modules, Geographical information, inverter, transformer specifications etc.)
First Time Charging Formats A to C ( includes details of T/L, transformer, bays, SLD, communication conformity, energy meter conformity etc.)
Undertaking by RE/Lead/Principal regarding discharging all operational and commercial responsibilities on behalf of generating stations as per the prevalent CERC Regulations.
Copy of application for connectivity which was submitted to CTU.
5. Undertaking to indemnify, defend and save the SLDCs/RLDCs harmless from any and all damages, losses including commercial losses.

## Slide 57: Forecasting Accuracy in Wind Forecast:
Chart: 
Chart: 

## Slide 58: Forecasting Accuracy in Wind Forecast:
Chart: 
Chart: 

## Slide 59
Wind Generation from Nov to March-
Helping in morning load ramp upto 7 a.m.
Not helping during peak load
Opposing during off peak period (increasing generation)
Chart: WR Demand Vs Wind on a typical day 06.07.2017
WR Demand | 37464.2463 | 36251.6242 | 36000.3427 | 35667.1719 | 35793.5278 | 37114.0114 | 37991.1389 | 38973.4848 | 39239.299 | 39834.0248 | 39968.3772 | 40135.336 | 39714.0089 | 39481.4793 | 40430.1416 | 40640.8715 | 39958.2313 | 39325.2795 | 38854.064 | 40750.1879 | 41089.2961 | 39979.6247 | 40941.3948 | 39918.1489
WR Wind | 5594.97 | 5882.92 | 5808.11 | 5795.69 | 5467.45 | 5486.69 | 5158.59 | 4909.89 | 5525.38 | 6031.31 | 6380.27 | 6506.8 | 6683.9 | 6869 | 6933.73 | 6875.04 | 6885.28 | 6585.68 | 6371.4 | 5542.61 | 5016.2 | 4546 | 4716.23 | 4499.19
Wind generation from April to Oct-
Supporting the WR demand by ramping up in the morning
Helping during Peak load
Ramping down in the evening

## Slide 60
Highest RES penetration
WR Net load on Highest RES day