## Slide 1: WELCOME TO RAJASTHAN SLDC Rajasthan Rajya Vidyut Prasaran Nigam Ltd.
Meeting On
Furnishing of Real Time/Daily Renewable Energy Generation Data

## Slide 2: RAJASTHAN SLDC Rajasthan Rajya Vidyut Prasaran Nigam Ltd.
Presentation by:
Sanjay Mathur
XEN (REMC), SLDC
Rajasthan Rajya Vidyut Prasaran Nigam Ltd.
Jaipur
Furnishing of Real Time/Daily Renewable Energy Generation Data

## Slide 3: LOCATION OF EXISTING WIND AND SOLAR PROJECTS IN RAJASTHAN (AS ON 31st MARCH, 2018)
385 MW
JODHPUR
3550 MW
JAISALMER
Wind Power 4290.95 MW
Solar Power 2246.21 MW
250 MW
BIKANER
1900 MW
JODHPUR
TOTAL : 6537.16 MW
Expected Addition by 2021-22 : 23000 MW
355 MW
Pratapgarh
95 MW Scattered
(Solar)

## Slide 4
PRESENT SCENARIO OF REAL TIME/DAILY RE GENERATION DATA -RAJASTHAN

## Slide 5
PRESENT STATUS OF RE GENERATORS
TELEMETRY APRROVAL BY SLDC GIVEN TO RE GENERATORS TO BE CONNECTED IN NEAR FUTURE
TYPE OF RE GENERATOR | NO. OF RE GENERATORS WHOSE SCHEME APPROVED BY SLDC
SOLAR | 8 (1095 MW)
WIND | 11 (2004 MW)
TOTAL | 19

## Slide 6
PRESENT STATUS OF RE GENERATORS
STATUS OF RE GENERATORS CONNECTED TO SLDC RAJASTHAN
TYPE | NOs. INTEGRATED | NOs. REPORTING | REPORTING % | MODE
SOLAR | 40(936 MW) | 32(825 MW) | 80 | GPRS
WIND | 7 (434 MW) | 1 (63 MW) | 14 | 
TOTAL | 47 | 33 | 70 | 

## Slide 7
ROAD MAP TO REAL TIME
RE GENERATION DATA -RAJASTHAN

## Slide 8: Proposed System Architecture for Smart Grid Initiative/ Platform in RVPN

## Slide 9: Broad objectives of SMART TRANSMISSION NETWORK & ASSET MANAGEMENT SYSTEM (STNAMS)
Visualization and Situational Awareness of Transmission Grid
System for Real time monitoring and Control of Substations and Grid
Decision Support System for maintaining of Voltage Profile and Reactive Power Management
Wide Area Monitoring and Protection
Accuracy of Data for Planning Studies, Forecasting and implementing of required analytics for Decision Making
Reactive Power Management
Grid Security and Stability Management
Remote Operation of Substations
Reliable Communication Backbone

## Slide 10
Proposed System Architecture for STNAMS

## Slide 11
Data Communication Network
Substation Infrastructure
STNAMS Control Center
Cyber Security
Firewall/Cyber Security
Internet
DC CORE
DCG
DCG
SS
SS
SS
SS
SS
Distt GSS
SS
Distt GSS
Distt GSS
Distt GSS
Distt GSS
Distt GSS
Distt GSS
5G DWDM Ring
5G DWDM Ring
Substation Infrastructure
SS
SLDC
REMC
STOMS DC
Regional Control Centre
ERP Data Centre
STOMS
Backup Centre
Detail in Main control architecture
UCM
Web
Server
Email
Server
SCADA
VSM
Service Provider MPLS Network
765/400/200/132KV
132KV
1G Ring
1G Ring
Centralized monitoring & operations
SCADA Integration
Video Surveillance integration
NMS
Switch
Router
LAN
MAIN SMART INTEGRATED OPERATION AND COMMAND CENTER
OPGW

## Slide 12: Various packages proposed under STNAMS
S. No. | Element | Description
1 | Package-A1 | SCADA/EMS System that includes field infrastructure (RTUs, DCUs, PMUs Interfacing/ adaption work at substations) and Main, Back-Up and Regional Control Centers (Servers, Printers & associated software’s)
2 | Package-A2 | Reactive Power Compensation Equipments such as Switchable Shunt Reactors, STATCOMs at various Locations in Rajasthan Transmission Grid.
3 | Package-B | Information and Communication Technology (ICT) Infrastructure which includes the data center (NMS, UCS, VMS, Cyber Security), routers, Switches etc. for connecting to all substations/ offices and Control Centers along-with the Auxiliary Power Supply System.
4 | Package-C | OPGW network which includes OPGW and its associated hardware accessories, approach cable and Fiber Optic Distribution panel.

## Slide 13: SCADA/EMS PACKAGE MAIN ELEMENTS PACKEAGE-A1
S. No. | Element | Description
1 | RTU/SAS Systems | 765 kV: 2 Nos. (Type-I: 2 Nos.) 400 kV: 10 Nos. (Type-I: 7 Nos., Type-II: 3 Nos.) 220 kV: 113 Nos. (Type-I: 5 Nos, Type-II: 61 Nos. and Type-III: 39 Nos. (New RTUs) & 19 Nos. (RTU Replacement) 132 kV: 394 Nos. (Type-I: 9 Nos, Type-II:14 Nos. and Type-III: 369 Nos.) All the Data Acquisition Devices Site Adaption works based on the Type of the Substations. Existing RTU/SAS System Available for Monitoring: 101/24 Nos. After Implementation: 429 Nos. more Substations shall come under monitoring and control.
2 | DCU, RAS & FAS System | DCUs, Remote Access System and Fault Analysis system for all locations
3 | PMU/ PDC System | 25 Nos. of PMUs and 1 PDC alongwith Related visualization software and storage system
4 | Decision Support System/ Control Centre | SCADA, ICCP, Power System Analysis, Automatic Demand Management, Web and Other Applications Software

## Slide 14: ICT PACKAGE-B MAIN ELEMENTS
S. No. | Element | Description
1 | DWDM Equipments Optical Backbone | Dense Wavelength Division Multiplexing Optical Backbone – At critical optical nodes around 62 Nos.
2 | IP/MPLS Nodes | IP/MPLS Routers and Ethernet Switches
3 | Data Centre | Core Switches, Core IP/MPLS Routers, Internet Routers
4 | Smart Integrated Operation & Command | Smart Grid Integrated Operation and Command Center including Wall Controller, Video Monitoring System, Unified Communication System, Cyber Security and Network Management System
5 | Tele-protection Interface/ Module | Tele-protection module/ interface for Tele-protection using PSN Network
PROJECT AWARDED IN JUNE,2017, UNDER EXECUTION

## Slide 15: OPGW PACKAGE-C MAIN ELEMENTS
S. No. | Element | Description
1 | Optical Ground Wire (OPGW) | 24/48 Fiber OPGW is proposed to be Laid. Total Rajasthan Power Fibernet POP Locations (RPF-POP) after Implementation: 580 Nos. Already Laid /being laid: OPGW: 1748.16 kM/ 1249.276 kM Locations: 42 Nos. (6 Nos. State/ Pvt. Generating Stations, 2 Nos. 765 kV, 12 Nos. 400 kV, 14 Nos. 220 kV & 8 Nos. 132 kV substations) Proposed Under Project: OPGW: 13770.80 kM Locations: 538 Nos. (16Nos. CTU/Generators/ Other STU, 2 Nos. 400 kV, 114 Nos. 220 kV and 406 Nos. 132 kV)
2 | Fiber Optic Distribution Frame | Distribution Frame for Termination of Fiber Optic Cable along-with necessary patch cords
PACKAGE (S) AWARDED IN SEP,2017

## Slide 16: BROAD OBJECTIVE OF SMART TRANSMISSION OPERATIONS MANAGEMENT SYSTEM (STOMS)
Automated and transparent operations related to ABT mechanism and other load dispatch functions
Improvement in operational efficiency and to ensure timely service to all beneficiaries
Effective tool to perform various business and operational functions
Monitoring and enforcing grid code compliance by constituents
Optimal scheduling and dispatch operations
Automate Meter Reading with Meter Data Validation
Energy Accounting and Billing
OA approvals
Deviation Settlements

## Slide 17: STATUS OF STOMS WITH SPECIAL REFERENCE TO RE GENERATION DATA
ABT METERS WITH DLMS PROTOCOL INSTALLED AT ALL RE GENERATORS WITH 100% REPORTING TO SERVER
DAILY DATA IS BEING POLED (ONCE IN 24 HOURS) BY THE SERVER FROM THE DCUs ATTACHED WITH THE ABT METERS DULY GPS TIME SYNCHRONISED AND STAMPED
OFFLINE SCHEDULING AND PREPARTION OF RE DSM IS IN PROGRESS
ONLINE SCHEDULING OF RE POWER STARTED AND SHALL REACH 100% BY MONTH END
ONLINE DSM BILL OF RE SHALL BE ISSUED THEREAFTER

## Slide 18: Screen shots-real time block wise data of re generators

## Slide 22
Live real time data of RE Generators on MDM module of STOMS project

## Slide 23: THANK YOU kale.va@rvpn.co.in mathur.sanjay@rvpn.co.in