## Slide 1
CEA-Furnishing Real Time/Daily Renewable Energy Generation Data associated issues
Follow up Meeting
04.05.2018
Presentation by -
STATE LOAD DESPATCH CENTRE MPPTCL, JABALPUR

## Slide 4
YEAR | ENERGY SUPPLY (MU) | WIND INJECTION (MU) | % OF WIND | SOLAR INJECTION (MU) | % OF SOLAR
2012-13 | 47858.32 | 570.99 | 1.19 | 11.75 | 0.02
2013-14 | 51952.48 | 515.63 | 0.99 | 242.86 | 0.47
2014-15 | 57406.79 | 632.37 | 1.10 | 610.71 | 1.06
2015-16 | 64148.66 | 1538.96 | 2.40 | 1118.81 | 1.74
2016-17 | 64247.57 | 3521.24 | 5.48 | 1368.15 | 2.13
2017-18 | 69206.88 | 4141.83 | 5.98 | 1845.04 | 2.67
CONTRIBUTION OF WIND & SOLAR IN ENERGY SUPPLY OF MP

## Slide 10: Status of Green Energy Corridor Project (Phase-I) Madhya Pradesh RENEWABLE ENERGY POWER EVACUATION WORKS
Govt. of India is encouraging establishment of Renewable Energy Projects under Clean Energy Development mechanism.
Madhya Pradesh State has also formulated various policies for development of these projects in the State Sector
To evacuate power from anticipated RE capacity addition of about 5847MW in next five years, MPPTCL has conducted system studies & identified required transmission system strengthening and interconnection works for upcoming RE projects.
Estimated Cost of works proposed for RE Projects in MP
Transmission System Strengthening Works :Rs.3575 Crore
(Phase I: Rs 2100 Crore + Phase II: Rs 1475 Crore)
(B) Interconnection works :Rs.1125 Crore
Total Estimated Cost (A+B) :Rs.4700 Crore
Phase-I Transmission System Strengthening Works amounting to Rs. 2100 Crore are proposed to be completed within 3 year.

## Slide 11: GREEN ENERGY CORRIDOR SCHEME (PHASE-I) (ANTICIPATED COMPLETION YEAR 2018-2019)
Sl.No. | Particulars | Nos./ Ckt. Km | 
1 | 400kV New Substations (Mandsaur, Sagar, Ujjain) | 3 | Nos.
2 | 400kV Line | 690 | Ckt. Km
3 | 400kV Reactors | 3 | Nos.
4 | 220kV New Substations (Sendhwa,Jaora,Gudgaon,Kanwan,Ratangarh,Susner,Sailana)(220kVS/s Suwasara excluded) | 7 | Nos.
5 | 220kV Line | 1164 | Ckt. Km
6 | 132kV Line | 1128 | Ckt. Km
7 | 132/33kV Addl. Transformer (Nalkheda, Vijaypur) | 2 | Nos.
11
To evacuate power from anticipated RE capacity addition, MPPTCL has conducted system studies & identified required transmission system strengthening and interconnection works for upcoming RE projects.

## Slide 12: Balancing Potential
Balancing Potential is different at any moment, it depends upon:-
Conventional Plant Availability and technical capabilities ( Plants on bar, Technical Minimum, start up and down time)
Availability of other flexibility in the system
Reservoir Level of Hydel Power Stations and dispatchability
Thermal Generation is available in large quantity and therefore the backbone of balancing RE
MP have total 3261 MW capacity of hydro for balancing of RE during real time operation

## Slide 13
MP was among the first states in the Country to have computerized SCADA system commissioned in 1983.
To provide real time grid data, SLDC is equipped with SCADA/EMS system developed by M/s GE T&D Ltd. under WR-ULDC project, functioning since 2016.
The SCADA/EMS system is having three control centers i.e. SLDC Jabalpur, Back up LDC at Bhopal and SUB-LD Indore exchanging data through ICCP.
The SCADA/EMS system is acquiring data from around 300 Nos of locations (EHV S/s, Generating Stations, IPP, renewable stations) and PGCIL S/S.
The Communication network comprises of Optical fiber backbone with PLCC, VSAT, Leased Circuits and combination of these .
13
SCADA/EMS SYSTEM & COMMUNICATION

## Slide 14: Integration of Renewable Energy Sources
Total Installed Capacity of 3929.79 MW from Renewable Energy Sources, as on 10.04.2018, integrated with MP grid is–
Small Hydro Including SSGS Hydro (65MW) : 80.7 MW
Biomass : 60.5 MW
MSW : 11.5 MW
Biogas : 2.4 MW
Bagasse : 53.8 MW
Wind : 2438.31 MW (Pooling Stations – 74 Nos)
Solar including Captive – 1282.58 MW (Polling Stations – 44 Nos)
Total RE installed Capacity – 3929.79 MW
MPNRED Target by 2022 - Wind – 6.2GW &
Solar – 5.67GW

## Slide 15
• IEC 60870-5-104/101 Protocol has been used for RE.
• Types of Communication System:
VSAT / Dedicated Leased Line / PLCC
• pooling Station are telemetered, however due to some technical difficulties availability of data at present to the tune of 99.35%. Efforts are being made to ensure 100% data availability.
• At present we are receiving feeder wise injection data of renewable substations. Now we are integrating with existing Scada for obtaining turbine/inverter wise real time telemetry as well. Few RE generators are already started furnishing real time turbine/inverter wise telemetry to SLDC.
• Aggregated monthly generation data are being submitted to CEA through email on a regular basis.

## Slide 16
• Separate Desk for RE has already been started functioning round the clock.
• This Desk shall carry out Forecasting, Scheduling and Deviation settlement of wind and solar generators
• Hon’ble MPERC has issued Forecasting, Scheduling, Deviation Settlement Mechanism and related matters for Wind AND Solar generating stations, Regulations 2018, on 12 April 2018.
• These Regulation shall be applicable to all wind generator having installed capacity of 10 mw and solar generators with an installed capacity of 5 mw and above.

## Slide 18
Type | Installed Cap. In MW | No. of Pooling station | Information Received (No. of Pooling Stations) | LVRT Complied (No. of Pooling Stations)
Wind | 1494.2 | 14 | 12 | 12
Solar | 244 | 4 | 4 | 4
LVRT Compliance Status of Wind and Solar Generators

## Slide 19: Compliance of Regulatory Requirements
All the Renewable Energy Generation Projects shall have to comply the following regulatory requirements before commissioning of project and getting connected with the MP Grid –
Deposition of registration fee of ` 5000/- for connectivity with the grid and registration with SLDC
Data Acquisition System facility for transfer of telemetry data to SLDC in accordance with SLDC guidelines.
Confirmation of installation of ABT meters of 0.2s accuracy class with AMR facility for data downloading at SLDC. Meter, modem & SIM details duly certified by MPPTCL or Discoms.
Single line diagram indicating the connectivity with the grid duly certified by MPPTCL or Discoms.
Copy of connection agreement with Discom or MPPTCL.
Information regarding sale of power to MPPMCL / Third party sale or to any other state (Copy of PPA & LTA).
Information regarding compliance of LVRT status.
Information regarding REMC project.
PTCC approval if required.

## Slide 20: Forecasting of Wind and Solar Generators
    At present the wind and solar generators are forecasting their generation on day ahead basis either through forecasting agency or by themselves .
    No real time revisions are being done by the Wind and Solar Generators except SECI solar power project selling Inter State.
    SLDC has appointed the forecasting agency for load forecasting of Wind and Solar Generation and following arrangements have already been done.
    The pooling station wise static data and historical telemetry data was already provided.
    Integration through SLDC SCADA for providing real time telemetry data.
    The forecasting agency is being provide the Pooling Stations wise load forecast of wind and solar generation and MP as a whole.

## Slide 21
  SAMAST : MP SLDC approach
  Integrated system for ABT, OA, Scheduling, Outage Planning, renewable & MIS
Scope of project
System Architecture
Project Cost : 3.02 Cr. Project Completion : Nov 2017 Funding: PSDF Grant

## Slide 22: Integrated ABT, Open Access and MIS Project under Implementation at SLDC
The new system shall have following additional/advanced features :
Web based scheduling.
Integration with existing AMR system.
Availability of Meter-wise/block-wise ABT meter data of each intra state entities on SLDC website.
Registration, web-based/online processing of application for STOA along with online tracking of open access charges.
Web based MIS including daily/monthly/annual reports, online management of outage of transmission elements.
Billing, collection and disbursement of charges under intra state ABT mechanism.
Forecasting, Scheduling and Deviation settlement of wind and solar generators.
REC mechanism and Integration of RE generators with MP grid,

## Slide 23
Thank You !